Product specification

| Product | CAT6 UTP SOLID 23AWG×4P | NO. |  | Page | 1/2 |
| --- | --- | --- | --- | --- | --- |
| Edition | 2 | Established Date | 1998-9-23 | Revised Date | 2008/7/23 |
| Approval |  | Checked |  | Finish |  |

Configuration & Physical Characters:

| Conductor | Material | Bare Copper |
| --- | --- | --- |
|  | Size | 23AWG |
|  | Construction | 1/0.575/0.585 ± 0.01mm |
| Insulation | Material | HD-PE |
|  | Thickness | MIN at any point: 0.15mm MAX AVG:0.23 mm |
|  | Diameter | 1.0/1.02/1.08/1.06 ± 0.03mm |
|  | Colors | Blue-White/Blue |
|  |  | Orange-White/Orange |
|  |  | Green-White/Green |
|  |  | Brown-White/Brown |
| 3. stranding | Material | Latin Cross (PE) |
| 4. Jacket | Material | PVC | LSOH | conductor insulation rip cord jacket |
|  | Thickness | MIN at any point: 0.40mm MAX AVG: 0.55mm |  |
|  | Diameter | 6.3 ± 0.3 |  |
|  | Colors | Assorted upon request |  |
|  | Marking | Assorted upon request |  |

Product specification

| Product | CAT6 UTP SOLID 23AWG×4P | NO. |  | Page | 2/2 |
| --- | --- | --- | --- | --- | --- |
| Edition | 2 | Established Date | 1998-9-23 | Revised Date | 2005-5-23 |
| Approval |  | Checked |  | Finish |  |

Electric Characters:

| 1. Spark Test | 2000 ± 250 VOC |
| --- | --- |
| 2. Conductor Resistance | MAX 9.38 Ω/100m at 20℃ |
| 3. Resistance Unbalance | MAX 5% |
| 4. Capacitance Unbalance | MAX 330pF/100m |
| 5. Mutual Capacitance | MAX 560pF/100m |
|  | Impedance (Ω) | RL (dB) | ATT (dB/100) | NEXT (dB) | Next Power Sum (dB) | ELFEXT (dB/100m) | ELFEXT Power Sum (dB/100m) |
| 772KHz | 100 ± 15 | 19.44 | 1.84 | 76.0 | 74.0 | 70.0 | 67.0 |
| 1MHz | 100 ± 15 | 20.00 | 2.04 | 74.30 | 72.3 | 67.8 | 64.8 |
| 4MHz | 100 ± 15 | 23.01 | 3.81 | 65.3 | 63.3 | 55.8 | 52.8 |
| 8MHz | 100 ± 15 | 24.52 | 5.35 | 60.8 | 58.8 | 49.7 | 46.7 |
| 10MHz | 100 ± 15 | 25.00 | 5.99 | 59.3 | 57.3 | 47.8 | 44.8 |
| 16MHz | 100 ± 15 | 25.00 | 7.60 | 562 | 54.2 | 43.7 | 40.7 |
| 20MHz | 100 ± 15 | 25.00 | 8.52 | 54.8 | 52.8 | 41.8 | 38.8 |
| 25MHz | 100 ± 15 | 24.32 | 9.57 | 53.3 | 51.3 | 39.8 | 36.8 |
| 31.25MHz | 100 ± 15 | 23.64 | 10.74 | 51.9 | 49.9 | 37.9 | 34.9 |
| 62.5MHz | 100 ± 15 | 21.54 | 15.48 | 47.4 | 45.4 | 31.9 | 28.9 |
| 100MHz | 100 ± 15 | 20.10 | 19.92 | 44.3 | 42.3 | 27.8 | 24.8 |
| 125MHz | 100 ± 22 | 19.42 | 22.49 | 42.8 | 40.8 | 25.9 | 22.9 |
| 200MHz | 100 ± 22 | 18.00 | 29.15 | 39.8 | 37.8 | 21.8 | 18.8 |
| 250MHz | 100 ± 32 | 17.32 | 33.04 | 38.3 | 36.3 | 19.8 | 16.8 |